12/13/19


County of San Diego

Department of Public Works, Flood Control

RE: JVR SOLAR FLOOD CONTROL REVIEW (HYDROLOGY COMPLIANCE WITH THE COUNTY HYDROLOGY MANUAL ONLY) 
For the next submittal, please include a separate document which responds to each of the comments listed below.  No response was provided to the previous comments.
REVIEW COMMENTS (for previous comments, additional information included in bold text):

1. Although they are similar, the reference used for the curve numbers used should be from Section 4.1.2 of the County’s Hydrology Manual (HM), not TR55.  Justification for the curve numbers used is not included in the current submittal.  The maps are included and so is the PZN value, but the individual values used, and the reference from the Hydrology Manual for each and the individual PZN related adjustments need to be included.
2. The workmap for the hydrology calculations should include underlying topography, calculation point locations, longest flow paths with up and downstream elevations.  Topographic data and elevations are still not included.
3. Additional information/justification/detail needs to be provided for the composite curve numbers used.  See #1 above.
4. Corps lag time needs to be calculated following the methodology outlined in HM Section 4.1.5.2.  Calculation performed following the required methodology appear to produce results that differ significantly from those included in the report.  The lag time calculations included appear to be from the previously used (non-county) methodology, and don’t match the actual values used which appear to follow County methodology.  Please include the County methodology calculation details.
5. The hydraulic work map needs to include:

5. Clearly labeled topographic data

5. Clearly labeled reach names corresponding to the names used in HEC-RAS

6. Please include topographic data to support the elevations used for the culvert roadway data.

7. All cross sections need to have:

7. Bank stations placed appropriately

7. Accurate downstream reach lengths

7. Appropriate Manning’s “n” values

7. Station elevation data on both ends that extend to contain the entire flow

7. Orientation that is perpendicular to the direction of flow.  Please see examples: right side of XS 7200, the left side of XS 11600, and both sides of XS 12800, 13200.

8. All HEC-RAS runs should be separate plans in the same project.
9. The proposed condition model should include anything proposed that might obstruct flow.

10. If there is justification as to why the proposed fencing across the watercourse would not cause a substantial or measurable impact that information should be included in the report, otherwise the potential obstruction due to the fencing (including the impacts of debris blockage) should be included in the modeling.

11. The report should also address velocities and scour with respect to footing depths.  Assumed to be deferred to final engineering.
12. The report conclusions and plans should demonstrate clearly that the panels and associated equipment are all elevated safely above the calculated water surface elevations in all locations.  Assumed to be deferred to final engineering.
13.  There are 3 plans in each project.  Either label and describe each or delete those that aren’t necessary.

14. There appear to be only minor changes between the pre and post models.  All of the changes should be described in the report.

15. It’s unclear how flow crosses the high railroad berm between XS 8000 and 4000.  An easy way to rectify this discrepancy would be to add a levee to the top of the berm and ineffective flow area in the left side for the area below the berm in the cross sections, otherwise more complex modeling may be required.

16. The area between XS 2800 to 1600 where the railroad berm crosses the channel should include cross sections along the berm to model the weir flow.

17. The workmap appears to include interpolated cross sections that are not in the model.

3

